G

APPENDIX G

General Notes for

Typical Water/Wastewater Main Joint ContractS

GENERAL

G

- All work shall be done in accordance with Specifications included in the contract documents.

- All existing utilities are shown at approximate locations and depths are based on the best available records and limited field data.  The Engineer does not certify that all utilities are shown. The Contractor shall verify exact locations, sizes, and depths of existing utilities before beginning construction (including ordering of pre-cast manholes and concrete pipe if applicable).  NO SEPARATE PAY ITEM.

- The Contractor shall coordinate all tie-ins with the on-site City of Dallas Inspector.

- The Contractor shall ensure that existing fire hydrants are accessible to fire trucks at all times.

- CAUTION!!  Existing underground utilities involved.  Call DIG TESS at 1-800-344-8377, 48 hours prior to construction for the location of any underground utilities involved in the area. NO SEPARATE PAY ITEM.

- The Contractor is responsible for the protection of ALL existing utilities and utility structures.  Power poles may have to be braced at Contractor’s expense.  Contractor shall support underground utilities when excavating or constructing under such utilities. NO SEPARATE PAY ITEM.

- Reference to Standard Drawings shall mean those shown in the Dallas Water Utilities Standard Drawings for Water and Wastewater Construction (latest edition).

- All items of work required to complete the work as shown or implied by the plans and specified in the Contract Documents which are not listed as a pay item in the proposal shall be considered incidental.

WATER DESIGN

- The existing water line is to be used as a service line until the proposed main has been tested, approved and placed in service.

- Abandon all valves on abandoned water mains as per DWU Standard Drawing 219. NO SEPARATE PAY ITEM.

- The Contractor shall salvage fire hydrants and deliver them to 2901 Municipal Street, Monday thru Friday between 8 a.m. and 4p.m.  Contact Lindell Gaskey or Juan Nino at 214-670-8970; 24 hours prior to delivery.

- All bends, tees, fire hydrants and plugs shall be restrained type fittings.  Compact fittings shall not be used.  All bends shall be blocked with Class “B” concrete as per DWU Standard Drawing pp.229-234.  All fire hydrants shall be installed per DWU Standard Drawing p.224.  Polywrap shall be used on all cast iron fittings and fire hydrant bases.

All water services are to be replaced from the proposed water main to the meter clearing all existing and proposed utilities and pavement.  Relocate and reset all water meter as required and reconnect to existing house services.  Install water deadheads to unimproved lots.

G

- Fire hydrant leads and barrels shall be set to grade established for the proposed paving. If the hydrant is not accessible because of existing ground conditions, the hydrant shall be raised with extension(s) as directed by the owner.

- *All R.C.C.P. water mains shall be installed with bonded joints.  All D.I. pipe and fittings shall be polywrapped.  All flanged connections are to be insulated as per DWU Standard Drawing 223.

- The Contractor shall sequence his construction such that no more than one fire hydrant is out of service at any given time.

- Backfill made on break repairs to existing water mains may have been made with crushed rock.  This could present a cave-in danger to a new ditch; therefore precautions should be taken by the Contractor.  NO SEPARATE PAY ITEM.

- If required by the City of Dallas Inspector, the Contractor shall install temporary water lines on both sides of the street until the new water main has been completed, tested, approved, and accepted by DWU. NO SEPARATE PAY ITEM.

- Water services greater than 30 feet shall be a minimum of 1 inch in diameter.

*Special Case

WASTEWATER DESIGN

- The Contractor shall verify the location of all wastewater laterals and construct new laterals from the wastewater main to the property line with cleanouts and reconnect to the existing laterals for all existing buildings.  Deep cut connections may be required.

- The contractor shall maintain existing wastewater service and flow at all times. NO SEPARATE PAY ITEM.

- Prior to reconnection of wastewater laterals, the Contractor shall verify whether the existing lateral is active or inactive.  The Contractor is required, as a minimum, to include T.V. survey & perform dye testing.  All laterals determined to be inactive shall not be reconnected.  The DWU Construction Superintendent shall approve all laterals targeted for reconnection. NO SEPARATE PAY ITEM.

- The Contractor shall verify the location of all wastewater laterals and reconnect approved, active laterals to the existing lateral.

- The backfill around manholes located in existing or proposed pavement shall be flowable backfill as per NCTCOG Specification Items 504.6.6 and 504.2.3.4. NO SEPARATE PAY ITEM.

Removal of existing MH’s, Wastewater Access Devices & Cleanouts is considered incidental unless noted otherwise.

G

PAVING REPLACEMENT

- For proposed paving, drainage, and traffic control plans see State of Texas Department of Transportation Plans of Proposed State Highway Improvement, Federal Aid Project, STP-97 (434) MM, CSJ: 0918-45-369, for ELAM ROAD, DALLAS COUNTY, FROM ST. AUGUSTINE ROAD TO ACRES DRIVE.

OR

For proposed paving and drainage plans in Coxville St. from Skyfrost east to Dead-end, see 311D _____________ and 421Q ______________.

- Temporary paving shall be used over all street, drive and sidewalk cuts (AND TRENCH) within proposed paving limits.  Permanent paving shall be used outside proposed paving limits.

- For all construction performed outside paving limits, the contractor will be required to make paving repairs in strict accordance with the City of Dallas Pavement Cut and Repair Standards Manual (latest edition).

TRAFFIC CONTROL

- The Contractor shall provide for the diversion of pedestrians and vehicles during the progress of work in a manner satisfactory to the on-site City of Dallas inspector and in accordance with the City of Dallas Traffic Barricade Manual, latest edition.  NO SEPARATE PAY ITEM.

- The Contractor is responsible for coordinating all new water and wastewater construction with the traffic control plan.  Supplemental traffic control needed for the water and wastewater construction shall meet TxDOT traffic control standards.

- The Contractor shall maintain vehicular traffic ingress and egress to private property at all times.

- The Contractor shall replace any pavement markings and signs that are removed or damaged during construction.  NO SEPARATE PAY ITEM.

EXTRA NOTES

G

- Shut down of water mains 20” and larger shall ONLY be done during winter months of October 1st thru April 1st. Actual time shall be determined by the Construction Engineer.

- Construct wastewater lateral cleanouts and water meter boxes in the proposed sidewalks where applicable.

- All existing culverts and ditches are to be restored satisfactory to the construction engineer.  No separate pay item

- The Contractor shall provide water services with deadheads and wastewater laterals with cleanouts to all unimproved lots.

- All proposed water mains shall be PVC C900 (DR-14) Class C+ Embedment, except as noted on the plans.

- All water mains with no profile shall have a minimum cover as follows: 6”, 8”, 10”, & 12” - 48” below finished street grade or 72” below unimproved grade.

- Abandon all manholes on abandoned wastewater mains per DWU Standard Drawing p.316.

- Construction ditches in the traffic lanes are to be backfilled or plated after each construction period.