CITY OF DALLAS

DESIGN CHECKLIST

Project Description: ________________________________________________________ Contract #: _______________ ______________% Review Date: July 30, 2026

| Acceptable | Needs Correction | Not Applicable | GENERAL ITEMS |
| --- | --- | --- | --- |
|  |  |  | Title block (refer to DWU Drafting Standard for Pipeline Projects, Pg. 4, Figure 3.1) |
|  |  |  | Engineer’s Seal, signature, and TBPE firm registration number |
|  |  |  | Correct Scale |
|  |  |  | Location Map |
|  |  |  | Mapsco pages |
|  |  |  | As built water and wastewater map numbers are shown on plans |
|  |  |  | Bud Holcomb map number |
|  |  |  | Two Benchmarks per design sheet (At least one must be Dallas Water Utilities B.M.) |
|  |  |  | North arrow |
|  |  |  | General notes |
|  |  |  | Caution notes |
|  |  |  | File and sheet number |
|  |  |  | DWU Contract # on plans |
|  |  |  | ROW width and owner information |
|  |  |  | Lot and Block Numbers |
|  |  |  | Lot dimensions |
|  |  |  | Street names |
|  |  |  | Existing utilities in area (gas, electric, cable, etc) |
|  |  |  | Power poles, signal lights, billboards, trees, fences, walls, etc. (label) |
|  |  |  | Existing pavement is labeled |
|  |  |  | Reference (FB, 411Q, 685W), type, and size of existing water |
|  |  |  | Existing pipe type, direction of flow, and reference (411Q) of existing wastewater |
|  |  |  | Existing and Proposed Storm Sewer pipe size and reference (421Q) |
|  |  |  | Stationing and ties to ROW/centerline |
|  |  |  | Existing and proposed easements are labeled (Type, size, bearings and dimensions, volume and page, etc, are shown on plans) |
|  |  |  | Stations at PI, PC, and PT of proposed water/wastewater mains |
|  |  |  | Proposed paving is shown |
|  |  |  | TxDOT Permit number shown on plans |
|  |  |  | DART Permit number is shown on plans |
|  |  |  | Railroad Crossing shown on plans |
|  |  |  | “Connect to” and “Install” notes in call-outs |
|  |  |  | Curve data information |
|  |  |  | Minimum radius maintained on water and wastewater mains (200’ on 8” PVC) |
|  |  |  | Proposed mains extend 5 feet past paving limits before tying in |
|  |  |  | No mains running parallel and under existing or proposed TxDOT pavement |
|  |  |  | Pavement cuts required (water and wastewater) beyond paving limits should be clearly labeled and must comply with PW&T Cut Manual |
|  |  |  | Mains under TxDOT pavement should cross at 90○ (if possible) and be encased |
|  |  |  | No appurtenances in TxDOT Pavement |
|  |  |  | All proposed mains 8” (w/ww) and larger are profiled |
|  |  |  | Design slopes are to the nearest tenth of a percent |
|  |  |  | Elevations are to the nearest hundredth |
|  |  |  | Minimum depth of cover as per section 2.5 and 3.5 of Pipeline Design Manual (4’ depth for pipes 8”-12”, 5’ depth for 16”, and 6’ for 20” and larger pipes where existing or proposed pavement is permanent) |
|  |  |  | Length, size, material, and embedment type for each main is specified in profile (must conform to approved materials) |
|  |  |  | Existing and proposed grades and ground lines are shown in profile |
|  |  |  | Crossing utilities are shown and given an elevation |
|  |  |  | Size of proposed pipe complies with Master Plan, if applicable |
|  |  |  | Correct TCEQ Protection called out for all water – wastewater crossings |
|  |  |  | Parallel mains are shown in profile with distance in feet right or left |
|  |  |  | Crossing large water or wastewater mains may require utility supports or BOTOC |
|  |  |  | Special consideration for mains in TCEQ Voluntary Cleanup Sites, landfills, areas of leaking underground storage tanks, or other possible contamination sites (check Environmental Points of Interest Layer in DWU GIS and refer to DWU Soil and GWMP) |
|  |  |  | Riprap required if velocity in creek or channel is greater than 10 ft/s for crossing or parallel mains. |

| Acceptable | Needs Correction | Not Applicable | WATER MAINS |
| --- | --- | --- | --- |
|  |  |  | New mains located towards the north or east side of the street R.O.W, where possible |
|  |  |  | Main is not closer than 3 feet from existing main (when running parallel) |
|  |  |  | Main is no closer than 3 feet from the edge of ROW |
|  |  |  | Size and type of pipe is shown (for services - 2” and larger should be shown) |
|  |  |  | Water main for meter vault should be 4’ deep at plug |
|  |  |  | Provide access manholes with blowoff valves at low points for dewatering mains 20” and larger |
|  |  |  | Provide 2” Corp. Stop in access manholes as directed by Distribution for mains 20” and larger |
|  |  |  | Provide monitoring stations and pitot manholes as directed by Distribution for mains 20” and larger |
|  |  |  | Request disposition from Distribution for all services 2” and larger (replacement and type of proposed service) |
|  |  |  | Upgrade unmetered fire lines to D.C. devices and vaults |
|  |  |  | Replace brick vaults with concrete vaults |
|  |  |  | Bollards in traffic areas for vertical facilities (i.e. fire hydrants) |
|  |  |  | Water main is no closer than 9 feet in all directions to wastewater main where possible (if this distance cannot be achieved refer to section 2.10.4 of Pipeline Design Manual) |
|  |  |  | Valves are designed such that 3 valves are required to isolate a section of main (max. of 4 valves allowed) |
|  |  |  | Total number of valves at a main intersection equals to number of lines leading out from intersection minus one (3 for a cross, 2 for a tee) |
|  |  |  | Valves located at street intersection and/or property line projection |
|  |  |  | Valves are not more than 1000’ apart for mains 24” diameter and less |
|  |  |  | Gate Valves for mains up to 42” / Butterfly valves for 48” and larger |
|  |  |  | Valves between fire hydrants/ Main line valves adjacent to fire hydrants |
|  |  |  | Only one fire hydrant is out of service when a 3-valve section is shut down |
|  |  |  | Fire hydrant or flush point at dead end mains |
|  |  |  | Fire hydrant spacing (700’ separation between hydrants in residential areas and 500’ in commercial areas) |
|  |  |  | Fire hydrants should be outside of radius of curb, when possible |
|  |  |  | No size on size tapping sleeves without permission from Distribution |
|  |  |  | Alignment of proposed main is parallel to R.O.W. or Center Line |
|  |  |  | Minimum slope is provided (0.10% or 0.05% if 0.10% cannot be achieved), no 0% slopes are allowed |
|  |  |  | Excessive high points avoided (if required, fire hydrant recommended at location for 16” and smaller) |
|  |  |  | Properly sized air release valves (refer to AWWA Manual M51) are provided at high points for mains 12” and larger |
|  |  |  | Minimum size for areas zoned industrial and manufacturing is 12” |

| Acceptable | Needs Correction | Not Applicable | WASTEWATER MAINS |
| --- | --- | --- | --- |
|  |  |  | Main is not located in the flowline of an existing creek or drainage area |
|  |  |  | Main is located in same location as existing wastewater, 6 to 12” below existing grade, if possible |
|  |  |  | Manhole is properly sized (refer to 3.12.1.4 of Pipeline Design Manual) |
|  |  |  | Manhole spacing per Section 3.12.1.3 of Pipeline Design Manual (500 feet separation for pipes 6-15”, 800 feet for pipes 18-30”, 1000 feet for pipes 36-48”, and 2000 feet for pipes 54” and larger) |
|  |  |  | Size, type of pipe, direction of flow and material is shown |
|  |  |  | Limits and conditions for abandonment of existing Wastewater mains are specified |
|  |  |  | Manhole spacing for collection systems with horizontal curvature does not exceed 300 feet |
|  |  |  | Manholes are located at point of curvature (PC) and at point of termination of curve (PT) |
|  |  |  | Main is straight between manholes and excessive depths are avoided, if possible |
|  |  |  | Drop manhole connection is used to minimize excessive depth differences (2 foot and larger difference between in and out requires drop) |
|  |  |  | Design slope provides a minimum velocity of 2 ft/s when pipe is flowing full and does not exceed the maximum slope allowed (refer to section 3.4.5 of Pipeline Design Manual) |
|  |  |  | Flowlines elevations are called out in profile |
|  |  |  | Wastewater main is sized to Master Plan or required (existing) capacity |
|  |  |  | Small wastewater mains connect top to top on larger wastewater mains |
|  |  |  | Cleanouts at end of mains are replaced with WWADs unless cover is less than 3.5 feet |
|  |  |  | Type S (sealed) manholes in creeks or areas in the 100-year floodplain |
|  |  |  | Manholes shorter than 3 feet, for mains larger than 48” diameter, or for mains in deep cuts require special (structural) design |
|  |  |  | No lateral connections to WW mains 18” and larger unless a gas sealed manhole is provided |
|  |  |  | Clear distance between the outside of adjacent pipes should not be less than 1 foot for manholes with more than one pipe entering and exiting the manhole |

Comments:

| _________________________________________________ | ________________ |
| --- | --- |
| Project Manager | Date |